DUCT HUMIDITY/TEMPERATURE TRANSMITTER

HTDT Series

The HTDT series incorporates:

* Highly Accurate RH Sensing Element
* Choice of analog outputs
* Precision Platinum RTD for Temperature
* Polycarbonate weatherproof enclosure
* S/S Probe
* AC/DC operation

PRODUCT HIGHLIGHTS

* Humidity range: 0-100%
* Accuracy available 2%, 3%, & 5%

ENGINEERING SPEC’S

* Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure
* External mounting tabs must be slotted & tapered away from enclosure to ease field installation
* Enclosure shall be complete with neoprene gasket for duct to enclosure seal
* Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection
* Cover must be hinged and securely attached in the open position
* Operating temperature range must be -40 to 50°C (-40 to 122°F)
* Cover must contain security screw as extra protection from opening
* Product shall be CE approved

|  |  |
| --- | --- |
| SPECIFICATIONS |  |
| HUMIDITY SENSOR TYPE | Thermoset polymer based capacitive |
| TEMPERATURE SENSOR TYPE | 1000Ω Platinum, IEC 751, 385 Alpha, thin film |
| HUMIDITY SENSOR ACCURACY | ±2, 3, or 5 %RH (5 to 95 %RH) |
| TEMPERATURE SENSOR ACCURACY | ±0.1% of span |
| SENSOR RESPONSE TIME | 15 seconds typical |
| MEASUREMENT RANGE | 0 to 100 %RH |
| HYSTERESIS | ±1.5 %RH maximum |
| REPEATABILITY | ±0.5 %RH typical |
| OPERATING TEMPERATURE | -40 to 50°C (-40 to 122°F) |
| OPERATING HUMIDITY | 0 to 95 %RH non-condensing |
| POWER SUPPLY | 24 Vac/Vdc, +/- 10% |
| CONSUMPTION | 22 mA maximum |
| INPUT VOLTAGE EFFECT | Negligible over specified operating range |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| OUTPUT SIGNAL | 4-20 mA, 0-5 Vdc, or 0-10 Vdc (factory configured) |
| OUTPUT DRIVE @ 24 VDC | Current: 550Ω max  Voltage: 10,000Ω min |
| INTERNAL ADJUSTMENTS | Clearly marked ZERO and SPAN pots |
| ENCLOSURE | B: Polycarbonate, UL94-V0, IP65 (NEMA 4X)  F: Same as B, with thread adapter (1/2” NPT to M15) and cable gland fitting |
| PROBE | 230mm (9”) length x 12.7mm (1/2”) diameter s/s with porous filter |
| TERMINATION | Screw terminal block (14 to 22 AWG) |
| COUNTRY OF ORIGIN | Canada |