





PARTICULATE MATTER DUCT SENSOR

PMDT Series

The PMDT Particulate Matter Sensor uses an optical sensor based on laser scattering principles and features innovative contamination-resistance technology to perform highly accurate and reliable PM measurements. With a continuous-operation lifetime of more than 8 years, the sensor will provide long-term reliability and high-resolution particle size binning for the detection of environmental dust and other particles.

The sensor is housed within an IP65 Polycarbonate enclosure to monitor PM levels in a duct. The sensor achieves excellent performance characteristics, including high accuracy and low power consumption to ensure stable long-term operation. The PMDT features both 4-20 mA and voltage outputs (0-5 / 0-10 Vdc) for simple integration into any building automation system to assure good indoor air quality. The device is also available with an RS-485 MS/TP network connection including either Modbus or BACnet® protocol.

PRODUCT HIGHLIGHTS

* Laser scatter method sensor
* Detection of environmental dusts and other particles
* Transparent cover for LCD viewing
* Four selectable PM particle size detection ranges
* Highly accurate and reliable PM measurements
* Network communication available (BACnet® or Modbus)

ENGINEERING SPEC’S

* Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure
* External mounting tabs must be slotted & tapered away from enclosure to ease field installation
* Enclosure shall be complete with neoprene gasket for duct to enclosure seal
* Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection
* Cover must be hinged and securely attached in the open position
* Cover must contain security screw as extra protection from opening
* Product shall be CE approved







SPECIFICATIONS

|  |  |
| --- | --- |
| DESCRIPTION | ENGINEERING SPEC |
| SENSOR | Laser scatter method |
| PARTICLE SIZE | PM1.0, PM2.5, PM4.0 or PM10 (selectable) |
| MASS CONENTRATION RANGE | 0 – 1000 ug/m3 |
| RESOLUTION | 1ug/m3 |
| ACCURACY | ±10ug/m3 (0 – 100ug/m3), ±10% (100 – 1000ug/m3) |
| RESPONSE TIME | 1 second |
| SENSOR LIFETIME | >8 years |
| ANALOG MODEL | Consumption: 75 mA max @ 24 Vdc, 100 mA max @ 24 Vdc  Output Signals: 4-20 mA (sourcing) or 0-5 Vdc / 0-10 Vdc (selectable)  Output Drive Capability: 550Ω max for current output, 5KΩ min for voltage output  Output Scale: 0 – 1000ug/m3 (menu selectable scales) |
| BACnet® MODEL | Consumption: 50 mA max @ 24 Vdc, 80 mA max @ 24 Vac Interface: MS/TP, 2-wire RS-485  Baud Rate: 9600, 19200, 38400, 57600, 76800, or 115200 (menu selectable) Address Range: 0 – 127 (menu selectable) |
| MODBUS MODEL | Consumption: 50 mA max @ 24 Vdc, 80 mA max @ 24 Vac Interface: MS/TP, 2-wire RS-485, RTU  Baud Rate: 9600, 19200, 38400, 57600, 76800, or 115200 (menu selectable)  Address Range: 1 – 255 (menu selectable) |
| LCD SIZE | 35mm W x 15mm H (1.4” x 0.6”) alpha-numeric 2 line x 8 characters |
| LCD BACKLIGHT | Enable or disable via menu |
| DISPLAY VALUES | 0 – 500 Air Quality Index or 0 – 1000ug/m3 |
| POWER SUPPLY | 24 Vac/dc ±20% (non-isolated half-wave rectified) |
| PROTECTION CIRCUITRY | Reverse voltage protected; overvoltage protected |
| OPERATING CONDITIONS | -10 to 60°C (14 to 140°F), 0 to 95 %RH non-condensing |
| STORAGE CONDITIONS | -40 to 70°C (-22 to 158°F), 0 to 95 %RH non-condensing |
| WIRING CONNECTIONS | Screw terminal block (14 to 22 AWG) |
| ENCLOSURE DIMENSIONS | 116 x 100 x 54 mm (4.6 x 3.9 x 2.1”) – Enclosure  152 x 22.5 mm (6 x 0.85”) - Probe |
| ENCLOSURE / PROBE MATERIAL | Polycarbonate (UL94V-0) |
| TRI-COLOR LED | Good Green (0 – 50ug/m3) Yellow (51 – 150ug/m3  Red (151 – 1000ug/m3) |
| PM ALARM RELAY (OPTIONAL) | Contact Ratings: Form C (NO + NC), 2A @ 140 Vac, 2A @ 30 Vdc Relay Setpoint + Hysteresis: Programmable via menu  Relay Time Delay: Programmable via menu |
| COUNTRY OF ORIGIN | Canada |