REMOTE SPOT WATER DETECTOR

WLDR Series

The WLDR series incorporates:

* Single-point standalone detection
* Fail-safe circuitry
* One Relay standard or Two Relay option
* NO/NC form C, relay output
* Weatherproof enclosure

PRODUCT HIGHLIGHTS

* Monitors variety of liquids
* Alarm on liquid detection, power failure, or internal failure
* Remote sensor terminal block with conductive pins
* Extension cable available with various lengths
* Tri color LED for operation status

SPECIFICATIONS

|  |  |
| --- | --- |
| SPECIFICATIONS |  |
| POWER SUPPLY  | 12 - 27 Vac/dc |
| SUPPLY CURRENT  | 125 mA max @ 24 Vac |
| OPERATING TEMPERATURE  | 0 to 50°C (32 to 122°F) |
| ENCLOSURE  | PC with hinged lid and gasket, IP65 |
| DIMENSIONS  | 133mm L x 80mm W x 64-90mm H (5.3” x 3.1564” x 2.5”- 3.5”) |
| ALARM OUTPUT(S) | Form C relay, rated 1 Amps @ 125 Vac/60Vdc (resistive load) |
| APPROVALS  | CE, RoHS |
| COUNTRY OF ORIGIN  | Canada |
|  |  |
|  |  |
|  |  |