PRESSURE WET GAUGE PRESSURE TRANSMITTER

PWGS Series

The PWGS series incorporates:

- Ranges -14.7 through 10,000 PSIG (-101.4 through 68947.6 kPa)

- DC inputs, current and voltage outputs

- 316L Stainless Steel has excellent corrosion resistance (comparable to grade 304 stainless)

- 1/4” NPT- Male

- Accuracy to ±0.5% FSO

PRODUCT HIGHLIGHTS

- Weather resistant for harsh environments

- Capacitance sensing element

- Fast response time

- NIST traceable calibration

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| ACCURACY AT CONSTANT TEMP | 0.5% F.S.O. |
| PRESSURE RANGES & OVERLOAD | See chart |
| SUPPLY VOLTAGE | 9-32VDC (4-20mA signal) max supply current @ 20mA 9-32VDC (0-5V signal) and 14-32VDC (0-10V signal) max supply current @ 11mA |
| OUTPUT | 4-20 mA (loop powered) 0-5 Vdc or 0-10 Vdc |
| MEDIA COMPATIBILITY | Sensor diaphragm: 316L Stainless steel (for range up to max pressure range 3,000 psi), 304 Stainless steels (from 4000 psi max pressure up to 10,000psi) Pressure connection: 316L Stainless steel |
| PRESSURE PORT | 1/4” to 18 NPT external |
| OPERATING TEMP. RANGE (SENSOR) | -40 to 125°C (-40 to 257°F) |
| CIRCUIT PROTECTION | Reverse polarity and miswire protection |
| DEGREE OF PROTECTION | IP67/NEMA 6X for models with factory cable IP65/Nema 4X for model with conduit connectivity |
| CERTIFICATION | CE,ROHS |
| STABILITY | 0.25% F.S. per year |
| COUNTRY OF ORIGIN | Canada |

| OPERATING PRESSURE RANGE | PROOF PRESSURE | BURST PRESSURE |
| --- | --- | --- |
| 15 PSI/-14.7 PSI | 2x | 50X |
| 30 PSI/-14.7 PSI | 2x | 50X |
| 60 PSI/-14.7 PSI | 2x | 50X |
| 100 PSI/-14.7 PSI | 2x | 50X |
| 150 PSI/-14.7 PSI | 2x | 50X |
| 15 PSI | 2x | 50X |
| 25 PSI | 2x | 50X |
| 50 PSI | 2x | 50X |
| 100 PSI | 2x | 50X |
| 150 PSI | 2x | 50X |
| 200 PSI | 2x | 50X |
| 250 PSI | 2x | 50X |
| 300 PSI | 2x | 50X |
| 500 PSI | 2x | 50X |
| 1,000 PSI | 2x | 50X |
| 3000 PSI | 2x | 5x (See note 1) |
| 5,000 PSI | 1.5X | 4X |
| 10,000 PSI | 1.2X | 3X |

Note 1: Burst rating for 3000 psi with 316L SS is 3x only