PRESSURE WET DIFFERENTIAL TRANSMITTER

PWRD Series

The differential pressure transmitter is designed with dual remote sensors that enable it to accept high pressure in several ranges up to 500 PSI, 30 Bar or 3000 kPa. All models can handle overload pressure 2X and burst pressure 10X the maximum full scale range.

Features include field selectable pressure ranges and output signal types, output reversal and slow damping, port swapping and bidirectional measurements for the most flexible applications. The pressure transmitter is fully factory calibrated and temperature compensated for the highest start-up accuracy.

PRODUCT HIGHLIGHTS

- Field selectable range

- Field selectable output: 0-5V , 0-10V or 4-20 mA(2-wire)

- FT-6 or armored cable available in different lengths

- Conduit connectivity available

- Switch selectable uni or bi-directional

- Hinged polycarbonate weatherproof enclosure

ENGINEERING SPEC’S

- Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure

- External mounting tabs must be slotted & tapered away from enclosure to ease field installation

- Enclosure shall be complete with neoprene gasket for duct to enclosure seal

- Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection

- Cover must be hinged and securely attached in the open position

- Operating range must be 0 to 60°C (32 to 140°F), 10 to 90 %RH, non-condensing

- Cover must contain security screw as extra protection from opening

- Product shall be CE approved

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| POWER SUPPLY | 24 Vac/dc SELV ( class 2) Supply |
| CONSUMPTION | Voltage Mode: DC=6mA, AC=16mA. Current Mode: DC=20mA, AC=38mA |
| OUTPUT SIGNAL | 4-20 mA , 0-5/0-10 Vdc (jumper selectable) |
| OUTPUT DRIVE | 500Ω max for current output 10KΩ min for voltage output |
| PROTECTION CIRCUITRY | Reverse voltage protected, transient protected |
| LCD | 3 ½ digit LCD display |
| ACCURACY | ±1% full scale for the three highest range ( ±2% for the lowest range) |
| STABILITY | ±0.25% FS typical (1 year) |
| PRESSURE RANGES | 4 per model (menu selectable) |
| MEDIA COMPATIBILITY | Any gas or liquid compatible with 316 Stainless steel |
| PROOF PRESSURE | 2X highest range per model |
| BURST PRESSURE | 10X highest range per model |
| MAXIMUM LINE PRESSURE | = highest model range |
| PRESSURE CYCLES | >50 million |
| SURGE DAMPING | 1-60 seconds averaging (menu selectable) |
| ZERO ADJUST | Push-button and remote input |
| SENSOR OPERATING RANGE | -40 to 105°C (-40 to 221°F) |
| OPERATING ENVIRONMENT | 0 to 60°C (32 to 140°F), 10 to 90 %RH non-condensing |
| CERTIFICATION | UL 60730 7 CSA E60730 UL E539555 file # |
| UL MODEL | MPWRDPXSL |
| PURPOSE OF CONTROL | Operating Control |
| TYPE OF ACTION | Type 1 |
| IMPULSE VOLTAGE | 330V |
| POLLUTION DEGREE | 2 |
| UL 2043 / ULC S142 COMPLIANT | Suitable for Use in Air Handling Spaces in Accordance with Section 300.22, (C) of the National Electrical Code |
| EU CONFORMITY | CE |
| PRESSURE CONNECTION | 1/4” NPT male |
| REMOTE SENSOR CABLE | S: FT-6 plenum rated A: Armored flexible S/S |
| WIRING CONNECTION | 14-22 AWG screw terminal block |
| ENCLOSURE | Polycarbonate, UL94-V0, IP65 (NEMA 4X) F style includes thread adapter (1/2” NPT to M16) and cable gland fitting |
| WEIGHT | 650g (22.9oz) – Including remote cables and sensors |
| COUNTRY OF ORIGIN | Canada |