ROOM CARBON DIOXIDE DETECTOR

CDD5X1 Series

The CDD5*10 series uses a highly accurate and reliable Non-dispersive Infrared (NDIR) sensor to monitor CO2, a precision thermistor to monitor temperature and a thermoset polymer based capacitance sensor to measure humidity levels combined with state-of-the-art digital linearization and temperature compensated circuitry in an attractive, low profile enclosure for room applications and provides 3 analog outputs. Optional setpoint slidepot, momentary override and adjustable relay output are also available.

PRODUCT HIGHLIGHTS

- Outputs CO2, Temperature, & RH levels

- Menu drive set-up

- 0-2000 or 20,000 (dual-channel) ppm CO2 ranges

- Patented self-calibration algorithm

- Guaranteed 5 year calibration interval

- Easily field calibrated

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| GAS TYPE DETECTED | Carbon Dioxide (CO2) |
| CO2 SIGNAL | Measurement Type: CDD5A & B – Non-Dispersive Infrared (NDIR) CDD5C & D – Dual Channel Non-Dispersive Infrared (NDIR), diffusion sampling Range: CDD5A & B – 0-2000ppm CDD5C & D – 0-20,000ppm standard, programmable span from 2000 to 20,000ppm Standard Accuracy: CDD5A & B - ±30ppm + 3% of reading with Auto Cal on CDD5C & D - ±75ppm or 10% of reading (whichever is greater) Temperature Dependence: 0.2% FS per °C Stability: CDD5A & B - <2% FS over life of sensor (15 years typical) CDD5C & D - <5% FS over life of sensor (15 years typical) Pressure Dependence: <0.13% of reading per mm Hg Altitude Correction: Programmable from 0-5000 ft via keypad Response Time: <2 minute for 90% step change typical Warm-up Time: <2 minutes |
| OPTIONAL TEMPERTATURE SIGNAL | Sensing Element: See chart below Range: 0 to 35°C (32 to 95°F) or 0 to 50°C (32 to 122°F) selectable via keypad |
| OPTIONAL RH SIGNAL | Sensing Element: Thermoset polymer based capacitive Accuracy: ±2 %RH Range: 0 to 100 %RH, non-condensing Hysteresis: ±3 %RH Response Time: 15 seconds typical Stability: ±1.2 %RH typical @ 50 %RH in 5 years |
| OPTIONAL RELAY OUTPUT | Contact Ratings: From A contact (N.O.), 2 Amps @ 140 Vac/30 Vdc Trip Point: CDD5 & B – Programmable 500 – 2000 ppm via keypad CDD5C & D – Programmable 500 – 15,000 ppm via keypad Relay Hysteresis: CDD5A & B – Programmable 25 – 200 ppm via keypad CDD5C & D – Programmable 25 – 5—ppm via keypad |
| OPTIONAL LCD DISPLAY | Resolution: 1ppm CO2 1 %RH, 1°C (1°F) Size: 35mm W x 15mm H (1.4” x 0.6”) alpha-numeric, 2 line x 8 character Backlight: Enable or disable via keypad |
| OPTIONAL OVERRIDE SWITCH | Front panel push-button available as two-wire dry-contact output |
| OPTIONAL SETPOINT CONTROL | Front panel push-buttons available as two-wire resistive output, 0-10 KΩ standard |
| POWER SUPPLY | 20-28 Vdc/ac (non-isolated half-wave rectified) |
| OUTPUT SIGNALS | Current: 4-20 mA (model CDD5A & C) Voltage: 0-5 Vdc or 0-10 Vdc (model CDD5B & D) |
| CONSUMPTIONS | Current: 145 mA max @ 24 Vdc, 260 mA max @ 24 Vac (with all options) Voltage: 85 mA max @ 24 Vdc, 150 mA max @ 24 Vac (with all options) |
| OUTPUT DRIVE CAPABILITY | Current: 550Ω max Voltage: 10 KΩ min |
| OUTPUT RESOLUTION | 10 bit PWM |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| OPERATING CONDITIONS | 0 to 50°C (32 to 122°F), 5 to 95 %RH, non-condensing |
| SENSOR COVERAGE AREA | 100m2 (1000ft2) typical |
| ENCLSOURE | Material: ABS, White Dimensions: 84mm W x 119mm H x 29mm D (3.3” x 4.7” x 1.15”) Protection: IP30 (NEMA 1) |
| WIRING | Screw terminal block (14 to 22 AWG) |
| COUNTRY OF ORIGIN | Canada |

| Sensor Code | Temperature Sensor Description | Accuracy |
| --- | --- | --- |
| 02 | 100Ω Platinum, IEC 751, 385 alpha, 2 wire, Class B | ± 0.3 °C (± 0.54 °F) @ 0 °C (32 °F) |
| 05 | 1,801 Ω NTC thermistor | ± 0.5 °C (± 0.9 °F) @ -20 - 50 °C (-4 - 122 °F) |
| 06 | 3,000 Ω NTC thermistor | ± 0.2 °C (± 0.36 °F) @ 0 - 70 °C (32 - 158 °F) |
| 07 | 10,000 Ω (type 3) NTC thermistor | ± 0.2 °C (± 0.36 °F) @ 0 - 70 °C (32 - 158 °F) |
| 08 | 2.252 KΩ NTC thermistor | ± 0.2 °C (± 0.36 °F) @ 0 - 70 °C (32 - 158 °F) |
| 12 | 1000Ω Platinum, IEC 751, 385 alpha, 2-wire, Class B | ± 0.3 °C (± 0.54 °F) @ 0 °C (32 °F) |
| 13 | 1000Ω Nickel, DIN 43760, 2-wire, Class B | ± 0.4 °C (± 0.72 °F) @ 0 °C (32 °F) |
| 14 | 10,000 Ω (Type 3) NTC thermistor c/w 11 KΩ shunt | ± 0.2 °C (± 0.36 °F) @ 0 - 70 °C (32 - 158 °F) |
| 20 | 20,000 Ω NTC thermistor | ± 0.2 °C (± 0.36 °F) @ 0 - 70 °C (32 - 158 °F) |
| 24 | 10,000 Ω (Type 2) NTC thermistor | ± 0.2 °C (± 0.36 °F) @ 0 - 70 °C (32 - 158 °F) |
| 59 | 10,000 Ω NTC thermistor | ± 1% @ 25°C (77°F), β25/85 = 3435 ± 1% |