AC CURRENT SENSOR

CS-652 Series

The CS-652 series incorporates:

- factory calibration

- self-powered and no insertion loss

- 4-20 mA Output

- average measurement

- solid-state reliability

- input / output isolation via current transformer

PRODUCT HIGHLIGHTS

- compact form factor

- solid, reliable mounting

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| MEASUREMENT RANGE | CS-652-R1: 0-10/20/50 Amps CS-652-R2: 0-50/100/150 Amps CS-652-200: 0-200 Amps |
| MAXIMUM INPUT CURRENT | CS-652-R1: 100 Amps continuous CS-652-R2: 150 Amps continuous CS-652-200: 250 Amps continuous |
| ACCURACY | CS-652-R1/R2: ±2% FSO, CS-652-200: ±1% FSO (5-100% of range) |
| SIGNAL | 4-20 mA |
| SENSOR POWER | 15 to 30 Vdc (loop-powered) |
| INSULATION CLASS | 600 Vac, insulated conductors |
| FREQUENCY | 50/60 Hz |
| RESPONSE TIME | 200 mS typical, 0-90% |
| OUTPUT LOAD | 250Ω typical |
| MAXIMUM LOAD | >600 Ω @ 24 Vdc |
| OPERATING TEMPERATURE | -15 to 60°C (5 to 140°F) |
| OPERATING HUMIDITY | 5 to 90 %RH non-condensing |
| TERMINAL BLOCK | 14 to 22 AWG |
| DIMENSIONS | 67mm W x 68.9mm H x 24.1mm D (2.65” x 2.7” x 0.95”) |
| SENSOR APERTURE | 20.3mm (0.8”) |
| ENCLOSURE MATERIAL | ABS/PC, UL94-V0 |
| AGENCY APPROVALS | cULus listed |