AC MINI CURRENT SENSOR

CS-652 Mini Series

The CS-652 mini series incorporates:

- factory calibration

- self-powered and no insertion loss

- 4-20 mA Output

- average measurement

- solid-state reliability

- input / output isolation via current transformer

PRODUCT HIGHLIGHTS

- compact form factor

- solid, reliable mounting

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| MEASUREMENT RANGE | 0-10, 20, or 50 Amps |
| MAXIMUM INPUT CURRENT | 100 Amps continuous |
| ACCURACY | ±1% FSO (5-100% of range) |
| SIGNAL OUTPUT | 4-20 mA |
| SENSOR POWER | 15-30 Vdc, loop-powered |
| INSULATION CLASS | 600 Vac, insulated conductors |
| FREQUENCY | 50/60 Hz |
| RESPONSE TIME | 250 mS typical, 0-95% |
| OUTPUT LOAD | 250Ω typical |
| MAXIMUM LOAD | >600Ω at 24 vdc |
| OPERATING TEMPERATURE | -15 to 60°C (5 to 140°F) |
| OPERATING HUMIDITY | 5 to 90 %RH non-condensing |
| TERMINAL BLOCK | 14 to 22 AWG |
| DIMENSIONS | 48mm W x 49mm H x 21mm D (1.9” x 1.93” x 0.83”) |
| SENSOR APERTURE | 11.4mm (0.45”) |
| ENCLOSURE MATERIAL | ABS/PC, UL94-V0 |
| AGENCY APPROVALS | cULus listed |