ANALOG INPUT WITH OPTICAL ISOLATION TO ANALOG OUTPUT

GT-AI Series

The GT-AI analog isolation module is a 3 way isolating analog signal re-scaling module with one input/output channel. It will accept one analog voltage or current input signal, isolate it and re-scale it to another voltage or current output signal. The I/O signals have several pre-calibrated, fixed ranges or may be custom calibrated for various offsets and spans and can be direct or reverse acting to provide signal inversion.

The device has an on-board transformer that provides power supply isolation and also has input/output signal isolation.

The GT-AI also includes a regulated +24 Vdc power output that can be used to power a transducer or a resistance input. It features top-adjust trim-pots for offset and gain control, source or sink capabilities and an LED power indicator. Various I/O signal types are easily selected with DIP switches.

PRODUCT HIGHLIGHTS

- Input/Output signal isolation

- Field selectable input/output ranges

- Direct or reverse acting

- Regulated power supply output

- Compact and economical

- Snap track mounted

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| POWER SUPPLY | 24 Vac ±10% |
| CONSUMPTION | 150 mA maximum |
| OPERATING CONDITIONS | 0 to 50°C (32 to 122°F) 5 to 95 %RH non-condensing |
| STORAGE CONDITIONS | -30 to 70°C (-22 to 158°F) 5 to 95 %RH non-condensing |
| WIRING CONNECTIONS | Screw terminal block (14 to 22 AWG) |
| ENCLOSURE | Snap track mounting 127mm L x 47mm W (5.0” x 3.25”) |
| WEIGHT | 285g (10oz) |
| POWER OUTPUT | Regulated Power Output: 24 Vdc ±10% @ 30 mA maximum (use to power an external sensor) |
| INPUT SIGNAL | Preset Voltage Range: 0-1, 0-5, 0-10, 0-15, 0-20, 1-5, 2-10, 3-15, and 4-20 Vdc Adjustable Voltage Offset: 0-20 Vdc Adjustable Voltage Span: 1-20 Vdc Voltage Impedance: >10 KΩ |
| PRESET CURRENT RANGE | 0-1, 0-20, and 4-20 mA |
| ADJUSTABLE CURRENT OFFSET | 0-15 mA |
| ADJUSTABLE CURRENT SPAN | 4-20 mA |
| CURRENT IMPEDANCE | 250 Ω (1 KΩ for 0-1 mA range) |
| OUTPUT SIGNAL | Preset Voltage Range: 0-5, 1-5, 0-10, and 0-20 Vdc Preset Voltage Offset: 0, 1, and 2 Vdc Preset Voltage Spans: 1, 3, 4, 5, 6, 7, 8, and 10 Vdc Adjustable Voltage Offset: 0-10 Vdc Adjustable Voltage Span: 1-20 Vdc Voltage Impedance: >10 KΩ |
| PRESENT CURRENT RANGE | 0-20 and 4-20 mA |
| PRESET CURRENT OFFSET | 0, 4, and 8 mA |
| PRESET CURRENT SPANS | 4-20 mA |
| CURRENT IMPEDANCE | 750Ω |
| CURRENT SIGNAL TYPE | Source or Sink (jumper selectable) |
| SIGNAL DIRECTION | Normal/Reversable via single jumper |
| ACCURACY | ±1% typical |
| COUNTRY OF ORIGIN | Canada |