OUTSIDE NETWORK HUMIDITY AND TEMPERATURE SENSOR WITH SUN AND WIND SHIELD

HNOB Series

The outside network humidity/temperature sensor uses a highly accurate and reliable Thermoset Polymer based capacitance humidity sensor to monitor humidity and temperature levels and transmit values via BACnet® or Modbus communication to a building automation system. A hinged, gasketed weatherproof PC enclosure provides ease of installation.

PRODUCT HIGHLIGHTS

- IP65 hinged enclosure

- Integrated sun and wind shield

- Temperature compensated RH sensor

- BACnet® or Modbus output

- Slotted mounting holes angled for ease of field installation

- Custom branding available

ENGINEERING SPEC’S

- Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure

- External mounting tabs must be slotted & tapered away from enclosure to ease field installation

- Enclosure shall be complete with neoprene gasket for duct to enclosure seal

- Cover must be hinged and securely attached in the open position

- Sun and Wind shield integrated on product

- Relay with configurable trip point for RH or temperature

- Operating range must be -40 to 50°C (-40 to 122°F)

- Cover must contain security screw as extra protection from opening

- Product shall be CE approved

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| RELATIVE HUMIDITY SENSOR |  |
| - ACCURACY | ±2, 3, or 5 %RH (5 to 95 %RH) |
| - RANGE | 0-100%RH |
| - RESOLUTION | 0.01%RH |
| - HYSTERESIS | ± 0.8%RH @ 25°C (77°F) |
| - RESPONSE TIME | 8 seconds |
| - STABILITY | <0.25%RH/year |
| TEMPERATURE SENSOR |  |
| - ACCURACY | ± 0.2°C |
| - RANGE | -40 - 50°C (-40 - 122°F) |
| - RESOLUTION | 0.01°C |
| - RESPONSE TIME | 2 seconds |
| - STABILITY | <0.03°C /year |
| NETWORK COMMUNICATION |  |
| - HARDWARE | MS/TP, 2-wire, RS-485 |
| - SOFTWARE | BACnet® or Modbus |
| - BAUD RATE | 9600, 19200, 38400, 57600, 76800, or 15200 |
| - ADDRESS RANGE | BACnet®: 0 to 127 Modbus: 1 to 255 |
| PROBE |  |
| - MATERIAL | Polycarbonate sun/wind shield with Stainless steel probe and porous filter |
| - DIMENSIONS | 132mm x 38mm (5.19” x 1.5”) |
| RELAY (OPTIONAL) |  |
| - CONTACTS | 0.5 A at 125 VAC / 1 A at 24 VDC |
| - SETPOINT | Relative Humidity: 1 TO 90%RH or Temperature: 5 TO 40°C (40 - 100°F) |
| ENCLOSURE |  |
| - MATERIAL | PC, UL94-V0 |
| - PROTECTION | IP65 (NEMA 4X) |
| - CONNECTION | A: Threaded ½” NPT E: Same as A, with ½” NPT to M16 adapter and cable gland |
| - DIMENSIONS | 82.5mm W x 76.2mm H x 52.0mm D (3.25" x 3.0" x 2.05") |
| GENERAL |  |
| - POWER SUPPLY | 24 Vac/dc ±10% typical, 28 Vac/dc maximum |
| - CONSUMPTION | 22mA @ 24Vdc, 70mA @24Vac |
| - OPERATING ENVIRONMENT | -40 to 50°C (-40 - 122°F) |
| - WIRING CONNECTION | Screw terminal block (14 to 22 AWG) |
| - COUNTRY OF ORIGIN | Canada |