ROOM HUMIDITY/TEMPERATURE TRANSMITTER

HTRC Series

The HTRC series incorporates:

- Precision RH and temperature sensing elements

- Selection of analog outputs

- Options such as override, fanspeed switch and communications jack

- LCD Display available

- AC/DC operation

PRODUCT HIGHLIGHTS

- Humidity Range: 0 to 100%

- Accuracies available: 2%, 3% & 5%

- attractive, low profile enclosure

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| TEMPERATURE | Sensor: Curve-matched thermistor Accuracy: ±0.2°C (±0.4°F) Range: 0 to 35°C (32 to 95°F) or 0 to 50°C (32 to 122°F), programmable Offset: ±5.0°C programmable Display Units: °C or °F programmable Display Resolution: 0.1° < 100°, 1° > 100° |
| HUMIDITY | RH Sensor: Thermoset polymer based capacitive Accuracy: ±2, 3, or 5 %RH from 5 to 95 %RH Range: 0 to 100 %RH non-condensing Temperature Compensation: 0 to 50°C (32 to 122°F) Hysteresis: ±3 %RH Response Time: 15 seconds typical Stability: ±1.2 %RH typical @ 50 %RH in 5 years Offset: ±20 %RH, programmable |
| POWER SUPPLY | 24 Vac/dc ±10% (non-isolated half-wave rectified) |
| CONSUMPTION | 60 mA max @ 24 Vdc |
| INPUT VOLTAGE EFFECT | Negligible over specified operating range |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| OUTPUT SIGNAL | 4-20 mA active (sourcing), 0-5 Vdc or 0-10 Vdc (specify when ordering) |
| OUTPUT RESOLUTION | 10 bit for all signals |
| OUTPUT DRIVE @ 24 VDC | Current: 550 Ω maximum Voltage: 10K Ω minimum |
| PROGRAMMING/SELECTION | Via internal push buttons and on-screen menu |
| OPERATING CONDITIONS | 0 to 50°C (32 to 122°F), 0 to 95 %RH non-condensing |
| WIRING CONNECTIONS | Screw terminal block (14 to 22 AWG) |
| ENCLOSURE | White ABS - IP30 (NEMA 1) 84mm W x 119mm H x 29mm D (3.3” x 4.7” x 1.15”) |
| OPTIONAL LCD DISPLAY | Range: 00.0 to 99.9, 3 digit Symbols: °C, °F %RH, OCC Display Size: 38.1mm x 16.5mm (1.5” x 0.65”) Digit Height: 11.43mm (0.45”) Backlight: Enable/disable via menu |
| OPTIONAL OVERRIDE | Type: Front panel, momentary push button, 2 wire dry contact Switch Ratings: N.O., SPST, 50 mA @ 12 Vdc |
| OPTIONAL OCCUPIED INPUT (INCLUDED WITH OVERRIDE OPTION) | Type: Digital input, 0-5 Vdc or dry contact to common Logic: Active low or active high, programmable Action: Causes “OCC” segment to light in display |
| OPTIONAL FAN SPEED SWITCH | Type: Side panel mount, 5 position switch Range: Off, Auto, Low, Medium, High Signal: Resistance: 0, 2, 4, 6, 8 KΩ, 2 wire output (custom ranges avail.) |
| OPTIONAL NETWORK COMM. | 3.5mm Phono Jack: Ring/Mid/Tip connections to a 3 pin terminal block |
| COUNTRY OF ORIGIN | Canada |