OUTSIDE TEMPERATURE AND HUMIDITY SENSOR

NTOA SERIES

The outside temperature and humidity sensor is installed on outside North facing wall, under the eaves which will provide protection from direct sunlight and wind.

PRODUCT HIGHLIGHTS

•	Temperature sensor and relative humidity sensor mounted in outside probe

•	Hinged gasketed enclosure designed for outdoor mounting

•	RS-485 network with either BACnet or Modbus protocol

•	Modbus parameters can be customized at factory.

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| TEMPERATURE SENSOR | Sensing Element: 20KΩ NTC Thermistor Accuracy: ±0.2°C (±0.4°F) curve matched Range: -40 to 50°C (-40 to 122°F) Resolution: 0.1° C/F |
| RH SENSOR | Sensing Element: Thermistor polymer based capacitive Accuracy: ±2 %RH Range: 0 to 100 %RH, non-condensing Resolution: 1 %RH Hysteresis: ±3 %RH Response Time: 15 seconds typical Stability: ±1.2 %RH typical @ 50 %RH in 5 years |
| PROBE | 20mm (0.8”) long x 28mm (1.1”) diameter, PVC hub with mesh filter |
| POWER SUPPLY | BACnet®: 24 Vac/dc ±10% (non-isolated half-wave rectified) Modbus: 15 to 30 Vac/dc (non-isolated half-wave rectified) |
| CONSUMPTION | BACnet®: 25 mA max @ 24 Vdc Modbus: 10 mA max @ 24 Vdc |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| WIRING CONNECTIONS | Screw terminal block (14 to 22 AWG) |
| COMMUNICATION | Hardware: 2 wire RS-485 Software: Native BACnet® or Modbus MS/TP protocol, Factory selectable Baud Rate: Locally set from 300 to 76800 MAC Address Range: BACnet® - 0-127 Modbus - 1-255 |
| OPERATING CONDITIONS | -40 to 50°C (-40 to 122°F), 0-95 %RH, non-condensing |
| ENCLOSURE | ABS, UL94-5VB, IP61 (NEMA 2) 114mm W x 84mm H x 53mm D (4.5” x 3.3” x 2.1”) |
| COUNTRY OF ORIGIN | Canada |