SPLIT-CORE AC CURRENT SENSOR

SC-652 Series

The SC-652 series incorporates:

- factory calibration

- self-powered and no insertion loss

- 4-20 mA Output

- average measurement

- solid-state reliability

- input / output isolation via current transformer

PRODUCT HIGHLIGHTS

- compact form factor

- solid, reliable mounting

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| MEASUREMENT RANGE | SC-652-R1: 0-20/40/60 Amps SC-652-R2: 0-50/100/150 Amps SC-652-200: 0-200 Amps |
| MAXIMUM INPUT CURRENT | SC-652-R1: 100 Amps continuous SC-652-R2: 150 Amps continuous SC-652-200: 250 Amps continuous |
| ACCURACY | SC-652-R1/R2: ±2% FSO, SC-652-200: ±1% FSO (5-100% of range) |
| SIGNAL | 4-20 mA |
| SENSOR POWER | 15 to 30 Vdc (loop-powered) |
| INSULATION CLASS | 600 Vac, insulated conductors |
| FREQUENCY | 50/60 Hz |
| RESPONSE TIME | 200 mS typical, 0-90% |
| OUTPUT LOAD | 250Ω typical |
| MAXIMUM LOAD | >600 Ω @ 24 Vdc |
| OPERATING TEMPERATURE | -15 to 60°C (5 to 140°F) |
| OPERATING HUMIDITY | 5 to 90 %RH non-condensing |
| TERMINAL BLOCK | 14 to 22 AWG |
| DIMENSIONS | 76mm W x 79mm H x 24.9mm D (3” x 3.1” x 0.98”) |
| SENSOR APERTURE | 20.3mm (0.8”) |
| ENCLOSURE MATERIAL | ABS/PC, UL94-V0 |
| AGENCY APPROVALS | cULus listed |