RIGID DUCT AVERAGE TEMPERATURE TRANSMITTER WITH LCD

TDDR Series

The multi-point rigid duct average temperature transmitter incorporates four precision platinum RTD’s encapsulated in a 6 mm (0.236”) OD, 304 stainless steel probe and is available in various lengths. All probes provide excellent heat transfer, fast response and resist moisture penetration. A transmitter that provides a high accuracy signal with excellent long-term stability, low hysteresis and fast response is available with various ranges. A hinged and gasketed Polycarbonate enclosure is included for ease of installation. An LCD is provided in either °C or °F.

PRODUCT HIGHLIGHTS

- Compact form factor enclosure with soft close cover

- IP 65 Enclosure

- Slotted mounting holes angled for ease of field installation

- Custom branding available

- Multiple mounting options

ENGINEERING SPEC’S

- Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure

- External mounting tabs must be slotted & tapered away from enclosure to ease field installation

- Probe shall be one piece 304 S.S fully potted

- Enclosure shall be complete with neoprene gasket for duct to enclosure seal

- Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection

- Cover must be hinged and securely attached in the open position

- Sensing range must be -40 to 60°C (-40 to 140°F)

- Cover must contain security screw as extra protection from opening

- Product shall be CE approved

| SPECIFICATIONS |  |
| --- | --- |
| SENSOR TYPE | 1000 Ω platinum RTD |
| SENSOR ACCURACY | ±0.3°C (±0.54°F) @ 0°C (32°F) |
| PROBE SENSING RANGE | -40 to 60°C (-40 to 140°F) |
| PROBE DIAMETER | 6mm (0.236”) |
| PROBE MATERIAL | 304 series stainless steel |
| STANDARD LENGTHS | 450, 600, 900 mm (18”, 24”, 36”) |
| OUTPUT SIGNAL | 4-20 mA current loop, 0-5 Vdc, or 0-10 Vdc (factory configured) |
| TRANSMITTER ACCURACY | ±0.2% of span, including linearity |
| POWER SUPPLY | 15-30 Vdc or 12-28 Vac |
| MAXIMUM LOOP CURRENT | 20 mA |
| MINIMUM LOOP CURRENT | 4 mA |
| MAXIMUM LOOP LOAD | 700Ω |
| MAXIMUM CURRENT (VOLTAGE) | 11 mA |
| MAXIMUM OUTPUT (VOLTAGE) | 10 Vdc |
| CONSUMPTION (MAX) | Current: 20 mA Voltage: 11 mA |
| INPUT VOLTAGE EFFECT | Negligible over specified operating range |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| OUTPUT DRIVE @ 24 VDC | Current: 700Ω max Voltage: 20,000Ω min |
| LCD DISPLAY UNITS | °C or °F (factory configured) |
| DISPLAY RANGE | 3 digit for -88.8 to 888 as required |
| DISPLAY SIZE | 38.1mm W x 16.5mm H (1.5” x 0.65”) |
| DIGIT HEIGHT | 11.4mm (0.45”) plus °C/°F symbol |
| AMBIENT OPERATING RANGE | 0 to 50°C (32 to 122°F), 5 to 95 %RH |
| ENCLOSURE | B: Grey polycarbonate UL94-V0, IP65 (NEMA 4X) F: Same as B with thread adapter (1/2” NPT to M16) and cable gland fitting |
| WIRING CONNECTIONS | Screw terminal block (14 to 22 AWG) |
| COUNTRY OF ORIGIN | Canada |