STAINLESS STEEL SURFACE TEMPERATURE SENSOR

TE200AS Series

The TE200AS series is a single gang, blank stainless-steel wall plate that incorporates precision temperature sensors used to monitor room temperatures where additional security is required. Additional options are available that include manual override.

PRODUCT HIGHLIGHTS

- Tamperproof mounting screws

- Custom ranges – to be specified at time of order

- Precision RTD element

- Insulating foam providing a thermal barrier from wall temperatures

- Two (2) wire or Three (3) connection to the Building Automation System depending on selected options.

- Custom Branding

| SPECIFICATIONS |  |
| --- | --- |
| SENSOR TYPE | 100 Ω Platinum, IEC 751, 385 Alpha, thin film 1801 Ω NTC Thermistor, ±0.2°C 3000 Ω NTC Thermistor, ±0.2°C 10,000 Ω Type 3, NTC Thermistor, ±0.2°C 2.252K Ω NTC Thermistor, ±0.2°C 1000 Ω Platinum, IEC 751, 385 Alpha, thin film 1000 Ω Nickel, Class B, DIN 43760 10,000 Ω Type 3, NTC Thermistor, ±0.2°C c/w 11K shunt resistor 20,000 Ω NTC Thermistor, ±0.2°C 10,000 Ω Type 2, NTC Thermistor, ±0.2°C 10,000 Ω @ 25°C, ±1%, B = 3435 ±1% (25/85) |
| TEMPERATURE RANGE | -20 to 60°C (-4 to 140°F) |
| AMBIENT OPERATING RANGE | -20 to 60°C (-4 to 140°F) |
| ENCLOSURE | Stainless Steel - IP50 (NEMA 1) |
| DIMENSIONS | 114.3mm L x 69.85mm W x 4.75mm D (4.5” x 2.75” x 0.1875”) |
| TERMINATION | Sensor Only: Pigtail 2 or 3 wire Sensor with Options: Terminal Block |
| COUNTRY OF ORIGIN | Canada |

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| TRANSMITTER OUTPUT SIGNAL | Current 4-20 mA Voltage 0-5 Vdc Voltage 0-10 Vdc |
| TRANSMITTER RANGES | 0 to 35°C (32 to 95°F) 0 to 50°C (32 to 122°F) Custom range, please contact Greystone |

TRANSMITTER OUTPUT SIGNAL