DESIGNER ROOM TEMPERATURE TRANSMITTER

TE500AD Series

The TE500AD series is an attractive, low profile enclosure that incorporates a precision platinum RTD and transmitter that provides a high accuracy signal with excellent long-term stability, low hysteresis and fast response for measurement of room temperatures

PRODUCT HIGHLIGHTS

- Precision RTD

- Mountable directly to a single gang electrical box or directly on wall

- Insulating foam providing a thermal barrier from wall temperatures

- Two (2) wire or Three (3) wire connection

- Custom branding available

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| OPERATING ENVIRONMENT | 0 to 70°C (32 to 158°F) |
| TEMPERATURE SENSOR | 1000 Ω Platinum RTD, IEC 751, 385 Alpha, thin film |
| SENSOR ACCURACY | ±0.3°C (±0.54°F) @ 0°C (32°F) |
| SIGNAL OUTPUT | 4-20 mA current loop, 0-5 Vdc, or 0-10 Vdc (factory configured) |
| TRANSMITTER ACCURACY | ±0.1% of span, including linearity |
| 4-20 mA LOOP POWER SUPPLY | 15-35 Vdc or 22-32 Vac |
| MINIMUM CURRENT LOOP | 2 mA nominal (occurs with shorted sensor) |
| MAXIMUM LOOP CURRENT | 22.5 mA nominal (occurs with open sensor) |
| MAXIMUM LOOP LOAD | >600Ω |
| 0-5 VDC POWER SUPPLY | 10-35 Vdc or 10-32 Vac |
| 0-10 VDC POWER SUPPLY | 15-35 Vdc or 15-32 Vac |
| MAXIMUM CURRENT (VOLTAGE) | 5 mA nominal |
| MAXIMUM OUTPUT (VOLTAGE) | Limited to <5.5 Vdc for 0-5 Vdc, <10.5 for 0-10 Vdc |
| INPUT VOLTAGE EFFECT | Negligible over specified operating range |
| RFI REJECTION | Good RFI rejection of normal frequencies |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| WIRING CONNECTION | Screw terminal block (14 to 22 AWG) & Pig Tail |
| ENCLOSURE | White ABS, IP20 (NEMA 1) |
| DIMENSIONS | 114.3mm L x 69.85mm W x 31.8mm D (4.5” x 2.75” x 1.25”) |
| COUNTRY OF ORIGIN | Canada |

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| TRANSMITTER OUTPUT SIGNAL | Current 4-20 mA Voltage 0-5 Vdc Voltage 0-10 Vdc |
| TRANSMITTER RANGES | 0 to 35°C (32 to 95°F) 0 to 50°C (32 to 122°F) Custom range, please contact Greystone |

TRANSMITTER OUTPUT SIGNAL