ALL PURPOSE DUCT/IMMERSION TEMPERATURE SENSOR

TSAP Series

The all-purpose single point temperature sensor utilizes a precision sensor encapsulated in a 6mm (0.236”), 304 series stainless steel probe and is available in various lengths. All probes provide excellent heat transfer, fast response and resistance to moisture penetration.

PRODUCT HIGHLIGHTS

- Compact form factor enclosure with soft close cover

- IP 65 Enclosure

- Slotted mounting holes angled for ease of field installation

- Custom branding available

- Multiple mounting options

- Thermowell adapters

- Customer branding

ENGINEERING SPEC’S

- Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure

- External mounting tabs must be slotted & tapered away from enclosure to ease field installation

- Enclosure shall be complete with neoprene gasket for duct to enclosure seal

- Probe – Enclosure connection shall be fully potted to eliminate probe condensation and guarantee IP65 (NEMA4X rating)

- Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection

- Cover must be hinged and securely attached in the open position

- Probe must be 6mm O.D 304 stainless steel, of different lengths to cover between 1/3 to 2/3 of duct width

- Sensing range must be -40 to 100°C (-40 to 212°F)

- Cover must contain security screw as extra protection from opening

- Product shall be CE approved

| SPECIFICATIONS |  |
| --- | --- |
| SENSOR TYPES | Thermistor or RTD - 100 Ω Platinum, IEC 751, 385 Alpha, thin film - 1801 Ω NTC Thermistor, ±0.2°C - 3000 Ω NTC Thermistor, ±0.2°C - 10,000 Ω Type 3, NTC Thermistor, ±0.2°C - 2.252K Ω NTC Thermistor, ±0.2°C - 1000 Ω Platinum, IEC 751, 385 Alpha, thin film - 1000 Ω Nickel, Class B, DIN 43760 - 10,000 Ω Type 3, NTC Thermistor, ±0.2°C c/w 11K shunt resistor - 20,000 Ω NTC Thermistor, ±0.2°C - 10,000 Ω Type 2, NTC Thermistor, ±0.2°C - 10,000 Ω, 25°C, ±1%, B = 3435 ±1% (25/85) |
| SENSOR ACCURACY | Thermistors: ±0.2°C (±0.36°F) @ 25°C (77°F) Platinum RTD’s: ±0.3°C (±0.54°F) @ 0°C (32°F) Nickel RTD’s: ±0.4°C (±0.72°F) @ 0°C (32°F) |
| PROBE SENSING RANGE | -40 to 100°C (-40 to 212°F) |
| AMBIENT OPERATING RANGE | -40 to 50°C (-40 to 122°F), 5 to 95 %RH non-condensing |
| WIRE MATERIAL | PVC insulated, parallel bonded, 22 AWG |
| PROBE MATERIAL | 304 series stainless steel |
| PROBE DIAMETER | 6 mm (0.236”) |
| STANDARD LENGTHS | 50, 100, 150, 200, 300, and 450 mm (2”, 4”, 6”, 8”, 12”, and 18”) |
| ENCLOSURE | ABS, UL94-V0, IP65 (NEMA 4X) C: includes terminal block E: same as C, with thread adapter (1/2” NPT to M16), and cable gland fitting |
| TERMINATION | A: pigtail, 2 or 3 wire C & E: terminal block, 2 or 3 wire |
| COUNTRY OF ORIGIN | Canada |