OUTSIDE TEMPERATURE SENSOR

TSOB Series

The single point outside air temperature sensor utilizes a precision sensor. All probes are constructed to provide excellent heat transfer, fast response and are potted to resist moisture penetration. A sun and wind shield is integrated into a weatherproof compact Polycarbonate enclosure with a hinged and gasketed cover for ease of installation.

PRODUCT HIGHLIGHTS

- Compact form factor enclosure with soft close cover

- IP 65 Enclosure

- Slotted mounting holes angled for ease of field installation

- Custom branding available

- Multiple mounting options

ENGINEERING SPEC’S

- Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure

- External mounting tabs must be slotted & tapered away from enclosure to ease field installation

- Enclosure shall be complete with neoprene gasket for duct to enclosure seal

- Probe – Enclosure connection shall be fully potted to eliminate probe condensation and guarantee IP65 (NEMA4X rating)

- Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection

- Sensing probe shall be protected from sun and/or wind with a protective polycarbonate shield

- Cover must be hinged and securely attached in the open position

- Probe must be one-piece 6mm O.D 304 stainless steel

- Sensing range must be -40 to 50°C (-40 to 122°F)

- Cover must contain security screw as extra protection from opening

- Product shall be CE approved

| SPECIFICATIONS |  |
| --- | --- |
| SENSOR TYPE | Thermistor or RTD (see ordering chart) |
| SENSOR ACCURACY | Thermistors: ±0.2°C (±0.36°F) @ 25°C (77°F) Platinum RTD’s: ±0.3°C (±0.54°F) @ 0°C (32°F) Nickel RTD’s: ±0.4°C (±0.72°F) @ 0°C (32°F) |
| PROBE SENSING RANGE | -40 to 50°C (-40 to 122°F) |
| AMBIENT OPERATING RANGE | -40 to 50°C (-40 to 122°F), 5 to 95 %RH non-condensing |
| WIRE MATERIAL | Thermistor or RTD (see ordering chart) |
| ENCLOSURE | A: Polycarbonate, UL94-V0, IP65 (NEMA 4X) C: Same as A, includes terminal block E: Same as C, with cable gland fitting |
| TERMINATION | A: Pigtail, 2 or 3 wire & E: Terminal block, 2 or 3 wire |
| COUNTRY OF ORIGIN | Canada |