OUTSIDE AIR TEMPERATURE SENSOR

TSOS Series

The single point outside air temperature sensor utilizes a precision sensor. All probes are constructed to provide excellent heat transfer, fast response, and are potted to resist moisture penetration. A sun and wind shield is integrated into a weatherproof compact Polycarbonate enclosure with a hinged and gasketed cover for ease of installation.

PRODUCT HIGHLIGHTS

- Compact form factor enclosure with soft close cover

- IP 65 Enclosure

- Fast response time

- Custom branding available

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| SENSOR TYPE | Thermistor or RTD - 100 Ω Platinum, IEC 751, 385 Alpha, thin film - 1801 Ω NTC Thermistor, ±0.2°C - 3000 Ω NTC Thermistor, ±0.2°C - 10,000 Ω Type 3, NTC Thermistor, ±0.2°C - 2.252K Ω NTC Thermistor, ±0.2°C - 1000 Ω Platinum, IEC 751, 385 Alpha, thin film - 1000 Ω Nickel, Class B, DIN 43760 - 10,000 Ω Type 3, NTC Thermistor, ±0.2°C c/w 11K shunt resistor - 20,000 Ω NTC Thermistor, ±0.2°C - 10,000 Ω Type 2, NTC Thermistor, ±0.2°C - 10,000 Ω, 25°C, ±1%, B = 3435 ±1% (25/85) |
| SENSOR ACCURACY | Thermistors: ±0.2°C (±0.36°F) @ 25°C (77°F) Platinum RTD’s: ±0.3°C (±0.54°F) @ 0°C (32°F) Nickel RTD’s: ±0.4°C (±0.72°F) @ 0°C (32°F) |
| PROBE SENSING RANGE | -40 to 50°C (-40 to 122°F) |
| AMBIENT OPERATING RANGE | -40 to 50°C (-40 to 122°F), 5 to 95 %RH non-condensing |
| WIRE MATERIAL | PVC insulated, parallel bonded, 22 AWG |
| PROBE MATERIAL | Machined Aluminum probe |
| ENCLOSURE | A: Polycarbonate, UL94-V0, IP65 (NEMA 4X) C: same as A, with a terminal block E: Same as C, with thread adapter and cable gland fitting |
| TERMINATION | A: Pigtail, 2 or 3 wire C & E: Terminal block, 2 or 3 wire |
| COUNTRY OF ORIGIN | Canada |