OUTSIDE TEMPERATURE TRANSMITTER

TXOS Series

The single point outside temperature transmitter utilizes a precision platinum RTD sensor. All probes are constructed to provide excellent heat transfer, fast response and are potted to resist moisture penetration. A sun and wind shield is integrated into the enclosure. It is provided in a weatherproof Polycarbonate enclosure. A transmitter that provides a high accuracy signal with excellent long-term stability, low hysteresis and fast response is available with various ranges.

PRODUCT HIGHLIGHTS

- Compact form factor enclosure with soft close cover

- IP 65 Enclosure

- Slotted mounting holes angled for ease of field installation

- Custom branding available

- Multiple mounting options

- Thermowell adapters

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| SENSOR TYPE | 1000 Ω platinum RTD |
| SENSOR ACCURACY | ±0.3°C (±0.54°F) @ 0°C (32°F) |
| PROBE SENSING RANGE | -40 to 50°C (-40 to 122°F) |
| WIRE MATERIAL | PVC insulated, parallel bonded, 22 AWG |
| SUN/WIND SHIELD | Grey PVC, vented |
| OUTPUT SIGNAL | 4-20 mA current loop, 0-5 Vdc, or 0-10 Vdc (factory configured) |
| TRANSMITTER ACCURACY | ±0.1% of span, including linearity |
| OUTPUT DRIVE @ 24 VDC | Current: 600 mA maximum Voltage: 10 KΩ minimum |
| POWER SUPPLY | 0-5 Vdc: 10-35 Vdc or 10-28 Vdc 0-10 Vdc: 15-35 Vdc or 15-28 Vdc 4-20 mA: 15-35 Vdc (loop-powered) or 22-28 Vdc |
| CURRENT CONSUMPTION | Current: 20 mA Voltage: 5 mA |
| MAXIMUM CURRENT (VOLTAGE) | 5 mA nominal |
| MAXIMUM OUTPUT (VOLTAGE) | Limited to <5.5 Vdc or 0-5 Vdc, <10.5 for 0-10 Vdc |
| INPUT VOLTAGE EFFECT | Negligible over specified operating range |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| AMBIENT OPERATING RANGE | -40 to 50°C (-40 to 122°F), 5 to 95 %RH non-condensing |
| ENCLOSURE | A: Polycarbonate, UL94-V0, IP65 (NEMA 4X) E: Same as A, with cable gland fitting |
| TERMINATION | Screw terminal block (14 to 22 AWG) |
| APPROVALS | CE |
| COUNTRY OF ORIGIN | Canada |