ROOM TEMPERATURE TRANSMITTER WITH LCD

TXRCL Series

The TXRCL series room temperature transmitter with LCD display is an attractive, low profile enclosure that incorporates a precision temperature sensor and a transmitter that provides a high accuracy signal with excellent long-term stability, low hysteresis and fast response for measurement of room temperatures. Additional options are available manual override, communications jack & fan speed control.

PRODUCT HIGHLIGHTS

- Compact form factor

- Mountable directly to a single gang electrical box or directly to a wall

- Custom branding available

PRODUCT SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| POWER SUPPLY | 24 Vac/dc ±10% (non-isolated half-wave rectified) |
| CONSUMPTION | 20 mA + (20 mA x number of outputs) max @ 24 Vdc |
| INPUT VOLTAGE EFFECT | Negligible over specified operating range |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| OUTPUT SIGNAL | 4-20 mA, 0-5 Vdc or 0-10 Vdc (factory configured) |
| OUTPUT RESOLUTION | 10 bit for all signals |
| OUTPUT DRIVE CAPABILITY | Current: 550Ω max Voltage: 10,000Ω min |
| PROGRAMMING AND SELECTION | Via push buttons and on-screen menu |
| OPERATING CONDITIONS | 0 to 50°C (32 to 122°F), 5 to 95 %RH non-condensing |
| WIRING CONNECTIONS | Screw Terminal block (14 to 22 AWG) |
| ENCLOSURE | White ABS, IP30 (NEMA 1) |
| ENCLOSURE DIMENSIONS | 84mm W x 117mm H x 29mm D (3.3” x 4.6” x 1.15”) |
| LCD DISPLAY | Size: 38.1mm W x 16.5mm H (1.5” x 0.65”) Digit Height: 11.43mm (0.45”) Symbols: °C, °F, OCC Backlight: Enable or disable via menu |
| TEMPERATURE | Accuracy: ±0.2°C (±0.4°F) Range: 0 to 35°C (32 to 95°F) or 0 to 50°C (32 to 122°F) programmable Offset: ±9°F programmable Units: °C or °F programmable Resolution: 0.5° < 100°, 1° > 100° |
| OPTIONAL OVERRIDE | Front Panel Push Button: 2 wire dry contact Switch Ratings: N.O., SPST, 50 mA @ 12 Vdc |
| OCCUPIED INPUT | Signal Type: Digital input,0/5 Vdc or dry contact to common Logic: Active low or active high, programmable Action: Causes “OCC” segment to light on LCD |
| COUNTRY OF ORIGIN | Canada |