CONDUCTIVE CABLE WATER DETECTOR

WLDC Series

The WLDC series incorporates:

- Conductive Cable for liquid detection

- Fail-safe circuitry

- One Relay standard or Two Relay option

- NO/NC form C, relay output

- Weatherproof enclosure

PRODUCT HIGHLIGHTS

- Monitors variety of liquids

- Alarm on liquid detection, power failure, or internal failure

- Two relay version can configure second relay for trouble detection instead of liquid detection

- Conductive Cable available in several lengths

- Non-conductive leader cable available with various lengths for remote conductive cable installation

- Tri color LED for operation status

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| POWER SUPPLY | 12 - 27 Vac/dc |
| SUPPLY CURRENT | 125 mA max @ 24 Vac |
| OPERATING TEMPERATURE | 0 to 50°C (32 to 122°F) |
| ENCLOSURE | PC with hinged lid and gasket, IP65 |
| DIMENSIONS | 133mm L x 80mm W x 64-90mm H (5.3” x 3.1564 ” x 2.5”- 3.5”) |
| ALARM OUTPUT(S) | Form C relay, rated 1 Amps @ 125 Vac/60Vdc (resistive load) |
| APPROVALS | CE, RoHS |
| COUNTRY OF ORIGIN | Canada |