AC MINI CURRENT SENSOR

CS-652 Mini Series

The CS-652 mini series incorporates:

* factory calibration
* self-powered and no insertion loss
* 4-20 mA Output
* average measurement
* solid-state reliability
* input / output isolation via current transformer

PRODUCT HIGHLIGHTS

* compact form factor
* solid, reliable mounting

SPECIFICATIONS

|  |  |
| --- | --- |
| SPECIFICATIONS |  |
| MEASUREMENT RANGE  | 0-10, 20, or 50 Amps |
| MAXIMUM INPUT CURRENT  | 100 Amps continuous |
| ACCURACY  | ±1% FSO (5-100% of range) |
| SIGNAL OUTPUT  | 4-20 mA |
| SENSOR POWER  | 15-30 Vdc, loop-powered |
| INSULATION CLASS  | 600 Vac, insulated conductors |
| FREQUENCY  | 50/60 Hz |
| RESPONSE TIME  | 250 mS typical, 0-95% |
| OUTPUT LOAD  | 250Ω typical |
| MAXIMUM LOAD  | >600Ω at 24 vdc |
| OPERATING TEMPERATURE  | -15 to 60°C (5 to 140°F) |
| OPERATING HUMIDITY  | 5 to 90 %RH non-condensing |
| TERMINAL BLOCK  | 14 to 22 AWG |
| DIMENSIONS  | 48mm W x 49mm H x 21mm D (1.9” x 1.93” x 0.83”) |
| SENSOR APERTURE  | 11.4mm (0.45”) |
| ENCLOSURE MATERIAL  | ABS/PC, UL94-V0 |
| AGENCY APPROVALS  | cULus listed |