MULTI-POINT AIR VELOCITY PITOT TUBES

MP Series

The MP series of Air Velocity Pitot Tubes can be used with air differential pressure transmitters to calculate airflow in larger ducts or in areas of turbulent airflow. The units come in pairs suitable for duct sizes up to 2 m (6.56’). To size the proper MP length, add 150 mm to the duct width to calculate for MP length required. Example: if the duct width is 500 mm wide: 500 mm + 150 mm = 650 mm. An MP length of 700 mm is required. The standard MP Series is constructed of durable ABS and are also available in optional 316 Stainless Steel.

PRODUCT HIGHLIGHTS

* Durable ABS construction
* Gaskets included for duct sealing
* Push on connectors for 6 mm ID PVC tubing
* Use with the LP3 or ULP Series air DP transmitters