

ALL PURPOSE DUCT NETWORK TEMPERATURE SENSOR

TNAP Series

The single point, all purpose duct/immersion network temperature sensor utilizes a precision sensor that is encapsulated in a 6mm (0.236”) OD, 304 series stainless steel probe and is available in various lengths. All probes are potted to provide excellent heat transfer, fast response and moisture resistance. A compact enclosure with a hinged and gasketed cover provides protection, security and ease of installation.

Features include a -40 to 100 °C (-40 to 212 °F) temperature measurement range, high accuracy and resolution, and auto-detect baud rate. The network temperature sensor includes network variables for the temperature reading, °C / °F units and a calibration offset.

PRODUCT HIGHLIGHTS

* Precision Thermistor sending element
* High accuracy transmitter
* Compact ABS enclosure

ENGINEERING SPEC’S

* Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure
* External mounting tabs must be slotted & tapered away from enclosure to ease field installation
* Enclosure shall be complete with neoprene gasket for duct to enclosure seal
* Probe – Enclosure connection shall be fully potted to eliminate probe condensation and guarantee IP65 (NEMA4X rating)
* Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection
* Cover must be hinged and securely attached in the open position
* Probe must be 6mm O.D 304 stainless steel, of different lengths to cover between 1/3 to 2/3 of duct width
* Sensing range must be -40 to 50°C (-40 to 122°F)
* Cover must contain security screw as extra protection from opening
* Product shall be CE approved

SPECIFICATIONS

|  |  |
| --- | --- |
| DESCRIPTION | ENGINEERING SPEC |
| POWER SUPPLY | BACnet®: 24 Vac/dc ±10% (non-isolated half-wave rectified)  Modbus: 24 Vac/dc ±20% (non-isolated half-wave rectified) |
| CONSUMPTION | BACnet®: 25 mA max @ 24 Vdc  Modbus: 10 mA max @ 24 Vdc |
| PROTECTION CIRCUITRY | Reverse voltage protected, transient protected |
| OPERATING ENVIRONMENT | -40 to 50°C (-40 to 122°F), 5 to 95 %RH non-condensing |
| TEMPERATURE SENSOR | 20 KΩ NTC thermistor |
| SENSOR ACCURACY | ±0.2°C (±0.36°F) @ 0 to 70°C (32 to 158°F) |
| PROBE SENSING RANGE | -40 to 100°C (-40 to 212°F) |
| RESOLUTION | 0.1°C/°F |
| PROBE MATERIAL | 304 series stainless steel |
| PROBE DIAMETER | 6mm (0.236”) |
| BACnet® INTERFACE | MS/TP, 2-wire RS-485 |
| MODBUS INTERFACE | MS/TP (RTU), 2-wire RS-485 |
| BAUD RATE | 9600, 19200, 38400, 57600, 76800 or 115200 (auto-detect) |
| ADDRESS RANGE | BACnet®: 0 to 127 (switch selectable)  Modbus: 1 to 255 (switch selectable) |
| SERIAL CONFIGURATION | 8N1 |
| MODBUS ERROR CHECKING | CRC-16 reverse (A001) |
| WIRING CONNECTION | Screw terminal block (14 to 22 AWG) |
| ENCLOSURE | ABS, UL94-V0, IP65  E style includes thread adapter (1/2” NPT to M16) and cable gland fitting |
| DIMENSIONS | 82.5mm W x 76.2mm H x 52.0mm D (3.25” x 3.0” x 2.05”) |
| PROBE LENGTHS | 2, 4, 6, 8, 12, 18” |
| COUNTRY OF ORIGIN | Canada |





**Greystone Energy Systems, Inc.**

150 English Dr. Moncton, NB E1E 4G7

+1 506 853 3057

[mail@greystoneenergy.com](mailto:mail@greystoneenergy.com) Page **1** of **1**

ES-TNAP